## BoQ1
eProcurement System for Organisations under MoD Created By: NANAK CHAND RAJORA Created Date/Time: 24-Dec-2018 04:31 PM Tender Title: Repair Maintenance of electrical system including repair and servicing to DG Sets Switchgears and Starters for sewage pumps under GE Utility Ambala Cantt Tender ID: 2018_MES_221529_2
Tender Inviting Authority: GE (UTILITY) AMBALA CANTT 2nd CALL
Name of Work : Repair / Maintenance of electrical system including repair and servicing to DG Sets, Switchgears and Starters for sewage pumps under GE (U) Ambala Cantt.
Contract No: GE (U)/AMB/45/2018-19
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | R D Bansal |  | LAKHANPAL ELECTRIC
[5 empty] | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | Servicing repair/ overhauling of DG set of capacity 82.5 KVA installed at SW No 15. Removing tappet cover and cylinder heads from DG set, grinding and polishing of cylinder heads, grinding of valve sets, grinding of inlet and exhaust valve after fixing new seats, calibration of injector, refitting cylinder head and tappet cover, changing of oil and replacement of defective parts including testing the DG sets on load complete as directed. Note: (a) New spare parts shall be measured and paid separately under respective items here in after as supply only. (b) Labour cost for fixing parts shall deemed to be included in the unit rate of quoted (c) Repair shall be carried out by authorised workshop of reputed manufacturer. Make - Kirloskar. | 1.00 | Each Job | 10.00 | 5000.00 | 5000.00 | 12000.00 | 12000.00 | 5000.00 | R D Bansal
2.00 | Supply only injector cup | 8.00 | Each | 10.00 | 500.00 | 4000.00 | 900.00 | 7200.00 | 4000.00 | R D Bansal
3.00 | Supply only injector barrel plunger | 8.00 | Each | 10.00 | 1000.00 | 8000.00 | 900.00 | 7200.00 | 7200.00 | LAKHANPAL ELECTRIC
4.00 | Supply only Push rod | 4.00 | Each | 10.00 | 500.00 | 2000.00 | 600.00 | 2400.00 | 2000.00 | R D Bansal
5.00 | Supply only water pump with hose pipe set complete | 1.00 | Each | 10.00 | 10000.00 | 10000.00 | 2500.00 | 2500.00 | 2500.00 | LAKHANPAL ELECTRIC
6.00 | Supply only exhaust manifold with packing | 2.00 | Each | 10.00 | 2000.00 | 4000.00 | 2500.00 | 5000.00 | 4000.00 | R D Bansal
7.00 | Supply only rubber spider | 1.00 | Each | 10.00 | 2000.00 | 2000.00 | 400.00 | 400.00 | 400.00 | LAKHANPAL ELECTRIC
8.00 | Supply only Thermostat | 1.00 | Each | 10.00 | 1500.00 | 1500.00 | 1900.00 | 1900.00 | 1500.00 | R D Bansal
9.00 | Supply only AVR suitable for 82.5 KVA alternator | 1.00 | Each | 10.00 | 5000.00 | 5000.00 | 2500.00 | 2500.00 | 2500.00 | LAKHANPAL ELECTRIC
10.00 | Supply only Inlet and exhaust valve pair. | 8.00 | Each | 10.00 | 250.00 | 2000.00 | 350.00 | 2800.00 | 2000.00 | R D Bansal
11.00 | Supply only Valve sheet insert | 16.00 | Each | 10.00 | 150.00 | 2400.00 | 250.00 | 4000.00 | 2400.00 | R D Bansal
12.00 | Supply only Inlet and exhaust valve guide | 16.00 | Each | 10.00 | 150.00 | 2400.00 | 100.00 | 1600.00 | 1600.00 | LAKHANPAL ELECTRIC
13.00 | Supply only Piston assy complete. | 8.00 | Each | 10.00 | 3000.00 | 24000.00 | 1600.00 | 12800.00 | 12800.00 | LAKHANPAL ELECTRIC
14.00 | Supply only Cylinder liner with joint ring | 8.00 | Each | 10.00 | 500.00 | 4000.00 | 800.00 | 6400.00 | 4000.00 | R D Bansal
15.00 | Supply only Set of joint | 1.00 | Each | 10.00 | 3000.00 | 3000.00 | 100.00 | 100.00 | 100.00 | LAKHANPAL ELECTRIC
16.00 | Supply only Gasket for head | 1.00 | Each | 10.00 | 5000.00 | 5000.00 | 600.00 | 600.00 | 600.00 | LAKHANPAL ELECTRIC
17.00 | Supply only Gear oil seal | 1.00 | Each | 10.00 | 500.00 | 500.00 | 600.00 | 600.00 | 500.00 | R D Bansal
18.00 | Supply only Oil seal | 1.00 | Each | 10.00 | 500.00 | 500.00 | 600.00 | 600.00 | 500.00 | R D Bansal
19.00 | Supply only Thermostat element | 1.00 | Each | 10.00 | 300.00 | 300.00 | 900.00 | 900.00 | 300.00 | R D Bansal
20.00 | Supply only Hose set | 1.00 | Each | 10.00 | 500.00 | 500.00 | 650.00 | 650.00 | 500.00 | R D Bansal
21.00 | Supply only Lub oil cooler | 1.00 | Each | 10.00 | 1000.00 | 1000.00 | 800.00 | 800.00 | 800.00 | LAKHANPAL ELECTRIC
22.00 | Supply only Lub oil pressure gauge | 1.00 | Each | 10.00 | 1000.00 | 1000.00 | 700.00 | 700.00 | 700.00 | LAKHANPAL ELECTRIC
23.00 | Supply only Flexible pipe | 1.00 | Each | 10.00 | 500.00 | 500.00 | 900.00 | 900.00 | 500.00 | R D Bansal
24.00 | Supply only Oil filter with assy Make:Mico | 2.00 | Each | 10.00 | 1500.00 | 3000.00 | 1500.00 | 3000.00 | 3000.00 | LAKHANPAL ELECTRIC, R D Bansal
25.00 | Supply only Diesel filter assy Make:Mico | 2.00 | Each | 10.00 | 2500.00 | 5000.00 | 1400.00 | 2800.00 | 2800.00 | LAKHANPAL ELECTRIC
26.00 | Description all as per item Ser No 01 above but DG set of capacity 62.5 KVA installed at SW No 09. Note: (a) New spare parts shall be measured and paid separately under respective items here in after as supply only. (b) Labour cost for fixing parts shall deemed to be included in the unit rate of quoted (c) Repair shall be carried out by authorised workshop of reputed manufacturer. Make:Kirloskar | 1.00 | Each Job | 10.00 | 5000.00 | 5000.00 | 12000.00 | 12000.00 | 5000.00 | R D Bansal
27.00 | Supply only injector cup | 6.00 | Each | 10.00 | 500.00 | 3000.00 | 700.00 | 4200.00 | 3000.00 | R D Bansal
28.00 | Supply only injector barrel plunger | 6.00 | Each | 10.00 | 1000.00 | 6000.00 | 650.00 | 3900.00 | 3900.00 | LAKHANPAL ELECTRIC
29.00 | Supply only Push rod | 6.00 | Each | 10.00 | 500.00 | 3000.00 | 500.00 | 3000.00 | 3000.00 | LAKHANPAL ELECTRIC, R D Bansal
30.00 | Supply only water pump with hose pipe set complete | 1.00 | Each | 10.00 | 8000.00 | 8000.00 | 1700.00 | 1700.00 | 1700.00 | LAKHANPAL ELECTRIC
31.00 | Supply only exhaust manifold with packing | 2.00 | Each | 10.00 | 2000.00 | 4000.00 | 1900.00 | 3800.00 | 3800.00 | LAKHANPAL ELECTRIC
32.00 | Supply only rubber spider | 1.00 | Each | 10.00 | 2000.00 | 2000.00 | 300.00 | 300.00 | 300.00 | LAKHANPAL ELECTRIC
33.00 | Supply only Thermostat | 1.00 | Each | 10.00 | 1500.00 | 1500.00 | 1600.00 | 1600.00 | 1500.00 | R D Bansal
34.00 | Supply only AVR suitable for 62.5 KVA alternator | 1.00 | Each | 10.00 | 5000.00 | 5000.00 | 2500.00 | 2500.00 | 2500.00 | LAKHANPAL ELECTRIC
35.00 | Supply only Inlet and exhaust valve pair | 6.00 | Each | 10.00 | 250.00 | 1500.00 | 250.00 | 1500.00 | 1500.00 | LAKHANPAL ELECTRIC, R D Bansal
36.00 | Supply only Valve sheet insert | 12.00 | Each | 10.00 | 150.00 | 1800.00 | 200.00 | 2400.00 | 1800.00 | R D Bansal
37.00 | Supply only Inlet and exhaust valve guide | 12.00 | Each | 10.00 | 150.00 | 1800.00 | 90.00 | 1080.00 | 1080.00 | LAKHANPAL ELECTRIC
38.00 | Supply only Piston assy complete | 6.00 | Each | 10.00 | 2500.00 | 15000.00 | 1100.00 | 6600.00 | 6600.00 | LAKHANPAL ELECTRIC
39.00 | Supply only Cylinder liner with joint ring | 6.00 | Each | 10.00 | 500.00 | 3000.00 | 1000.00 | 6000.00 | 3000.00 | R D Bansal
40.00 | Supply only Set of joint | 1.00 | Each | 10.00 | 3000.00 | 3000.00 | 900.00 | 900.00 | 900.00 | LAKHANPAL ELECTRIC
41.00 | Supply only Gasket for head | 1.00 | Each | 10.00 | 5000.00 | 5000.00 | 650.00 | 650.00 | 650.00 | LAKHANPAL ELECTRIC
42.00 | Supply only Gear oil seal | 1.00 | Each | 10.00 | 500.00 | 500.00 | 450.00 | 450.00 | 450.00 | LAKHANPAL ELECTRIC
43.00 | Supply only Oil seal | 1.00 | Each | 10.00 | 500.00 | 500.00 | 500.00 | 500.00 | 500.00 | LAKHANPAL ELECTRIC, R D Bansal
44.00 | Supply only Thermostat element | 1.00 | Each | 10.00 | 300.00 | 300.00 | 900.00 | 900.00 | 300.00 | R D Bansal
45.00 | Supply only Hose set | 1.00 | Each | 10.00 | 500.00 | 500.00 | 500.00 | 500.00 | 500.00 | LAKHANPAL ELECTRIC, R D Bansal
46.00 | Supply only Lub oil cooler | 1.00 | Each | 10.00 | 1000.00 | 1000.00 | 900.00 | 900.00 | 900.00 | LAKHANPAL ELECTRIC
47.00 | Supply only Lub oil pressure gauge | 1.00 | Each | 10.00 | 1000.00 | 1000.00 | 600.00 | 600.00 | 600.00 | LAKHANPAL ELECTRIC
48.00 | Supply only Flexible pipe | 1.00 | Each | 10.00 | 500.00 | 500.00 | 900.00 | 900.00 | 500.00 | R D Bansal
49.00 | Supply only Oil filter with assy Make:Mico | 2.00 | Each | 10.00 | 1500.00 | 3000.00 | 1500.00 | 3000.00 | 3000.00 | LAKHANPAL ELECTRIC, R D Bansal
50.00 | Supply only Diesel filter assy Make:Mico | 2.00 | Each | 10.00 | 2200.00 | 4400.00 | 1400.00 | 2800.00 | 2800.00 | LAKHANPAL ELECTRIC
51.00 | Servicing repair/ overhauling of DG set capacity 50 KVA installed at SW No 04. Removing tappet cover and cylinder heads from DG set, grinding and polishing of cylinder heads, grinding of valve sets, grinding of inlet and exhaust valve after fixing new seats, refitting cylinder head and tappet cover, changing of oil and replacement of defective parts including testing the DG sets on load complete as directed. Note: (a) New spare parts shall be measured and paid separately under respective items here in after as supply only. (b) Labour cost for fixing parts shall deemed to be included in the unit rate of quoted (c) Repair shall be carried out by authorised workshop of reputed manufacturer. Make: Kirloskar. | 1.00 | Each Job | 10.00 | 5000.00 | 5000.00 | 10000.00 | 10000.00 | 5000.00 | R D Bansal
52.00 | Supply only Bearing C/R B.074.4.00.013 for 50 KVA DG Set. | 1.00 | Each | 10.00 | 1000.00 | 1000.00 | 1200.00 | 1200.00 | 1000.00 | R D Bansal
53.00 | Supply only Inlet and exhaust valve pair | 6.00 | Each | 10.00 | 500.00 | 3000.00 | 220.00 | 1320.00 | 1320.00 | LAKHANPAL ELECTRIC
54.00 | Supply only Valve sheet insert | 12.00 | Each | 10.00 | 500.00 | 6000.00 | 220.00 | 2640.00 | 2640.00 | LAKHANPAL ELECTRIC
55.00 | Supply only Inlet and exhaust valve guide | 12.00 | Each | 10.00 | 200.00 | 2400.00 | 70.00 | 840.00 | 840.00 | LAKHANPAL ELECTRIC
56.00 | Supply only Piston assy complete | 6.00 | Each | 10.00 | 1500.00 | 9000.00 | 900.00 | 5400.00 | 5400.00 | LAKHANPAL ELECTRIC
57.00 | Supply only Cylinder liner with joint ring | 6.00 | Each | 10.00 | 1000.00 | 6000.00 | 700.00 | 4200.00 | 4200.00 | LAKHANPAL ELECTRIC
58.00 | Supply only Set of joint | 1.00 | Each | 10.00 | 1500.00 | 1500.00 | 550.00 | 550.00 | 550.00 | LAKHANPAL ELECTRIC
59.00 | Supply only Gasket for head | 1.00 | Each | 10.00 | 5000.00 | 5000.00 | 550.00 | 550.00 | 550.00 | LAKHANPAL ELECTRIC
60.00 | Supply only Gear oil seal | 1.00 | Each | 10.00 | 250.00 | 250.00 | 450.00 | 450.00 | 250.00 | R D Bansal
61.00 | Supply only Oil seal | 1.00 | Each | 10.00 | 150.00 | 150.00 | 550.00 | 550.00 | 150.00 | R D Bansal
62.00 | Supply only Thermostat element | 1.00 | Each | 10.00 | 150.00 | 150.00 | 600.00 | 600.00 | 150.00 | R D Bansal
63.00 | Supply only Hose set | 1.00 | Each | 10.00 | 500.00 | 500.00 | 600.00 | 600.00 | 500.00 | R D Bansal
64.00 | Supply only Lub oil cooler | 1.00 | Each | 10.00 | 500.00 | 500.00 | 950.00 | 950.00 | 500.00 | R D Bansal
65.00 | Supply only Lub oil pressure gauge | 1.00 | Each | 10.00 | 1000.00 | 1000.00 | 700.00 | 700.00 | 700.00 | LAKHANPAL ELECTRIC
66.00 | Supply only Flexible pipe | 1.00 | Each | 10.00 | 500.00 | 500.00 | 900.00 | 900.00 | 500.00 | R D Bansal
67.00 | Supply only Sensor unit | 1.00 | Each | 10.00 | 1000.00 | 1000.00 | 400.00 | 400.00 | 400.00 | LAKHANPAL ELECTRIC
68.00 | Supply only Starter ring 121 teeth | 1.00 | Each | 10.00 | 4000.00 | 4000.00 | 700.00 | 700.00 | 700.00 | LAKHANPAL ELECTRIC
69.00 | Supply only WP assy | 1.00 | Each | 10.00 | 1000.00 | 1000.00 | 1500.00 | 1500.00 | 1000.00 | R D Bansal
70.00 | Supply only LO cooler & head assy | 1.00 | Each | 10.00 | 1000.00 | 1000.00 | 1500.00 | 1500.00 | 1000.00 | R D Bansal
71.00 | Supply only K.oil premium | 5.00 | Ltr | 10.00 | 500.00 | 2500.00 | 290.00 | 1450.00 | 1450.00 | LAKHANPAL ELECTRIC
72.00 | Supply only Fuel pipe | 2.00 | Each | 10.00 | 1000.00 | 2000.00 | 300.00 | 600.00 | 600.00 | LAKHANPAL ELECTRIC
73.00 | Supply only Banded wrapped belt | 2.00 | Each | 10.00 | 500.00 | 1000.00 | 800.00 | 1600.00 | 1000.00 | R D Bansal
74.00 | Supply only Oil filter with assy Make:Mico | 2.00 | Each | 10.00 | 1500.00 | 3000.00 | 1400.00 | 2800.00 | 2800.00 | LAKHANPAL ELECTRIC
75.00 | Supply only Diesel filter assy Make:Mico | 2.00 | Each | 10.00 | 2200.00 | 4400.00 | 1200.00 | 2400.00 | 2400.00 | LAKHANPAL ELECTRIC
76.00 | Servicing repair/ overhauling of DG set capacity 43 KVA installed at SW No 12. Removing tappet cover and cylinder heads from DG set, grinding and polishing of cylinder heads, grinding of valve sets, grinding of inlet and exhaust valve after fixing new seats, refitting cylinder head and tappet cover, changing of oil and replacement of defective parts including testing the DG sets on load complete as directed. Note: (a) New spare parts shall be measured and paid separately under respective items here in after as supply only. (b) Labour cost for fixing parts shall deemed to be included in the unit rate of quoted (c) Repair shall be carried out by authorised workshop of reputed manufacturer. Make: Kirloskar. | 1.00 | Each Job | 10.00 | 5000.00 | 5000.00 | 8000.00 | 8000.00 | 5000.00 | R D Bansal
77.00 | Supply only Inlet and exhaust valve pair | 3.00 | Each | 10.00 | 1000.00 | 3000.00 | 250.00 | 750.00 | 750.00 | LAKHANPAL ELECTRIC
78.00 | Supply only Valve sheet insert | 6.00 | Each | 10.00 | 500.00 | 3000.00 | 250.00 | 1500.00 | 1500.00 | LAKHANPAL ELECTRIC
79.00 | Supply only Inlet and exhaust valve guide | 6.00 | Each | 10.00 | 500.00 | 3000.00 | 60.00 | 360.00 | 360.00 | LAKHANPAL ELECTRIC
80.00 | Supply only Piston assy complete | 3.00 | Each | 10.00 | 200.00 | 600.00 | 1000.00 | 3000.00 | 600.00 | R D Bansal
81.00 | Supply only Cylinder liner with joint ring | 3.00 | Each | 10.00 | 1500.00 | 4500.00 | 1000.00 | 3000.00 | 3000.00 | LAKHANPAL ELECTRIC
82.00 | Supply only Set of joint | 1.00 | Each | 10.00 | 1000.00 | 1000.00 | 500.00 | 500.00 | 500.00 | LAKHANPAL ELECTRIC
83.00 | Supply only Gasket for head | 1.00 | Each | 10.00 | 1500.00 | 1500.00 | 500.00 | 500.00 | 500.00 | LAKHANPAL ELECTRIC
84.00 | Supply only Gear oil seal | 1.00 | Each | 10.00 | 1000.00 | 1000.00 | 400.00 | 400.00 | 400.00 | LAKHANPAL ELECTRIC
85.00 | Supply only Oil seal | 1.00 | Each | 10.00 | 250.00 | 250.00 | 400.00 | 400.00 | 250.00 | R D Bansal
86.00 | Supply only Thermostat element | 1.00 | Each | 10.00 | 150.00 | 150.00 | 500.00 | 500.00 | 150.00 | R D Bansal
87.00 | Supply only Hose set | 1.00 | Each | 10.00 | 150.00 | 150.00 | 300.00 | 300.00 | 150.00 | R D Bansal
88.00 | Supply only Lub oil cooler | 1.00 | Each | 10.00 | 500.00 | 500.00 | 500.00 | 500.00 | 500.00 | LAKHANPAL ELECTRIC, R D Bansal
89.00 | Supply only Lub oil pressure gauge | 1.00 | Each | 10.00 | 1000.00 | 1000.00 | 450.00 | 450.00 | 450.00 | LAKHANPAL ELECTRIC
90.00 | Supply only Flexible pipe | 1.00 | Each | 10.00 | 500.00 | 500.00 | 500.00 | 500.00 | 500.00 | LAKHANPAL ELECTRIC, R D Bansal
91.00 | Supply only Sensor unit | 1.00 | Each | 10.00 | 500.00 | 500.00 | 320.00 | 320.00 | 320.00 | LAKHANPAL ELECTRIC
92.00 | Supply only Starter ring 121 teeth | 1.00 | Each | 10.00 | 3000.00 | 3000.00 | 690.00 | 690.00 | 690.00 | LAKHANPAL ELECTRIC
93.00 | Supply only LO cooler & head assy | 1.00 | Each | 10.00 | 4000.00 | 4000.00 | 1400.00 | 1400.00 | 1400.00 | LAKHANPAL ELECTRIC
94.00 | Supply only K.oil premium | 6.00 | Ltr | 10.00 | 500.00 | 3000.00 | 290.00 | 1740.00 | 1740.00 | LAKHANPAL ELECTRIC
95.00 | Supply only Fuel pipe | 2.00 | Each | 10.00 | 1000.00 | 2000.00 | 250.00 | 500.00 | 500.00 | LAKHANPAL ELECTRIC
96.00 | Supply only Banded wrapped belt | 2.00 | Each | 10.00 | 500.00 | 1000.00 | 680.00 | 1360.00 | 1000.00 | R D Bansal
97.00 | Disconnecting and removing the radiator assy from DG set of capacity 82.5 KVA and transporting it to the workshop to carry out the repair/overhauling, descaling the radiator tubes and fins by circulating descaling solution, bracing the damaged/leaking radiators tubes,welding the top and bottom tank complete and making it leak proof. Reinstalling in position connecting and testing complete all as directed. Make as per existing: Kirloskar | 1.00 | Each Job | 10.00 | 4000.00 | 4000.00 | 3500.00 | 3500.00 | 3500.00 | LAKHANPAL ELECTRIC
98.00 | Description all as per srl item No 97 here in before but of capacity 62.5 KVA Make as per existing: Kirloskar. | 1.00 | Each Job | 10.00 | 4000.00 | 4000.00 | 3500.00 | 3500.00 | 3500.00 | LAKHANPAL ELECTRIC
99.00 | Description all as per srl item No 97 here in before but of capacity 50 KVA. Make as per existing: Kirloskar. | 1.00 | Each Job | 10.00 | 4000.00 | 4000.00 | 300.00 | 300.00 | 300.00 | LAKHANPAL ELECTRIC
100.00 | Description all as per srl item No 97 here in before but of capacity 43 KVA. Make as per existing: Kirloskar. Note for 97 to 100: (a) Spares parts required for replacement shall be measured and paid for separately under respective items here in after as supply only. (b) Labour cost for fixing parts shall deemed to be included in the unit rate of quoted. (c) Repair shall be carried out by authorised workshop of reputed manufacturer. | 1.00 | Each Job | 10.00 | 3500.00 | 3500.00 | 7000.00 | 7000.00 | 3500.00 | R D Bansal
101.00 | Disconnecting and removing the self starter 24 volts from DG set and transporting it to the workshop to carry out the repair/overhauling including replacement of defective worn out parts and reassembling the same DG set and testing complete all as specified and directed by Eng-in-Charge. Note: (a) Spares parts required for replacement shall be measured and paid for separately under respective items of schedule as supply only. (b) Labour cost for fixing parts shall deemed to be included in the unit rate of quoted. (c) Repair shall be carried out by authorised workshop of reputed manufacturer. Make as per existing: Kirloskar. | 2.00 | Each Job | 10.00 | 5000.00 | 10000.00 | 1500.00 | 3000.00 | 3000.00 | LAKHANPAL ELECTRIC
102.00 | Supply only Steel pinion. Make as per existing: Lucas. | 2.00 | Each | 10.00 | 2000.00 | 4000.00 | 700.00 | 1400.00 | 1400.00 | LAKHANPAL ELECTRIC
103.00 | Supply only Clutch assy. Make as per existing: Lucas. | 2.00 | Each | 10.00 | 4000.00 | 8000.00 | 700.00 | 1400.00 | 1400.00 | LAKHANPAL ELECTRIC
104.00 | Supply only Solenoid switch. Make as per existing: Lucas. | 2.00 | Each | 10.00 | 500.00 | 1000.00 | 1200.00 | 2400.00 | 1000.00 | R D Bansal
105.00 | Supply only Carbon brush. Make as per existing: Lucas. | 2.00 | Each | 10.00 | 500.00 | 1000.00 | 200.00 | 400.00 | 400.00 | LAKHANPAL ELECTRIC
106.00 | Description all as per srl item No 101 here in before but of capacity 12 Volts -ditto-. Note: (a) Spares parts required for replacement shall be measured and paid for separately under respective items of schedule as supply only. (b) Labour cost for fixing parts shall deemed to be included in the unit rate of quoted. (c) Repair shall be carried out by authorised workshop of reputed manufacturer. Make as per existing: Kirloskar. | 2.00 | Each Job | 10.00 | 4000.00 | 8000.00 | 1000.00 | 2000.00 | 2000.00 | LAKHANPAL ELECTRIC
107.00 | Supply only Steel pinion. Make as per existing: Lucas. | 2.00 | Each | 10.00 | 2000.00 | 4000.00 | 600.00 | 1200.00 | 1200.00 | LAKHANPAL ELECTRIC
108.00 | Supply only Clutch assy. Make as per existing: Lucas. | 2.00 | Each | 10.00 | 4000.00 | 8000.00 | 600.00 | 1200.00 | 1200.00 | LAKHANPAL ELECTRIC
109.00 | Supply only Solenoid switch. Make as per existing: Lucas. | 2.00 | Each | 10.00 | 500.00 | 1000.00 | 1200.00 | 2400.00 | 1000.00 | R D Bansal
110.00 | Supply only Carbon brush. Make as per existing: Lucas. | 2.00 | Each | 10.00 | 500.00 | 1000.00 | 200.00 | 400.00 | 400.00 | LAKHANPAL ELECTRIC
111.00 | Dismantling/disconnecting the worn out winding of stator of the alternator of capacity 82.5 KVA DG set by moving and shifting the stator to the workshop including winding the stator with super enammeled copper conductor wire of existing gauge including insulating material and varnish etc complete all as specified and directed by Eng-in-Charge. | 1.00 | Each Job | 10.00 | 25000.00 | 25000.00 | 35000.00 | 35000.00 | 25000.00 | R D Bansal
112.00 | Description all as per srl item No 111 here in before but of capacity 43 KVA -ditto-. Note for 111 and 112: Winding shall be carried out by authorised workshop of reputed manufacturer. | 1.00 | Each Job | 10.00 | 20000.00 | 20000.00 | 20000.00 | 20000.00 | 20000.00 | LAKHANPAL ELECTRIC, R D Bansal
113.00 | Supply and fix in replacement Ammeter 96x96 sqmm, 0-200 Amp digital type complete all as specified and directed by Eng-in-Charge. | 3.00 | Each | 10.00 | 1000.00 | 3000.00 | 900.00 | 2700.00 | 2700.00 | LAKHANPAL ELECTRIC
114.00 | Supply and fix in replacement voltmeter 96x96 sqmm, 0-500 Amp digital type complete all as specified and directed by Eng-in-Charge. | 3.00 | Each | 10.00 | 1000.00 | 3000.00 | 900.00 | 2700.00 | 2700.00 | LAKHANPAL ELECTRIC
115.00 | Supply and fix in repair rectifier 24 plates in 3 stacks complete all as specified and directed by Eng-in-Charge. Make: IRI/AE. | 3.00 | Each | 10.00 | 4000.00 | 12000.00 | 1000.00 | 3000.00 | 3000.00 | LAKHANPAL ELECTRIC
116.00 | Supply and fix in replacement automatic voltage regulator (AVR) suitable for 43-62.5 KVA DG set complete all as specified and directed by Eng-in-Charge. Make as per existing: National | 3.00 | Each | 10.00 | 5000.00 | 15000.00 | 2500.00 | 7500.00 | 7500.00 | LAKHANPAL ELECTRIC
117.00 | Supply and fix in replacement auto matic voltage regulator (AVR) suitable for 82.5 KVA DG set complete all as specified and directed by Eng-in-Charge. Make as per existing: National | 1.00 | Each | 10.00 | 6000.00 | 6000.00 | 2500.00 | 2500.00 | 2500.00 | LAKHANPAL ELECTRIC
118.00 | Calibration of fuel injection pump for DG set for 43/50 KVA and replacement of defective parts of the pump complete all as specified and directed by Eng-in-Charge. Note (a) Spares parts required for replacement shall be measured and paid for separately under respective items of schedule as supply only. | 2.00 | Each Job | 10.00 | 4000.00 | 8000.00 | 2500.00 | 5000.00 | 5000.00 | LAKHANPAL ELECTRIC
119.00 | Supply only Element. Make as per existing: Mico. | 12.00 | Each | 10.00 | 400.00 | 4800.00 | 250.00 | 3000.00 | 3000.00 | LAKHANPAL ELECTRIC
120.00 | Supply only Delivery valve. Make as per existing: Mico. | 12.00 | Each | 10.00 | 400.00 | 4800.00 | 200.00 | 2400.00 | 2400.00 | LAKHANPAL ELECTRIC
121.00 | Supply only Bearing of existing one. Make as per existing: Mico. | 12.00 | Each | 10.00 | 500.00 | 6000.00 | 200.00 | 2400.00 | 2400.00 | LAKHANPAL ELECTRIC
122.00 | Supply only Pump seal. Make as per existing: Mico. | 6.00 | Each | 10.00 | 250.00 | 1500.00 | 300.00 | 1800.00 | 1500.00 | R D Bansal
123.00 | S&F in replacement of self starter 12 volts suitable for 43 to 50 KVA DG set complete all as directed by Eng-in-Charge.Make as per existing: Lucas. | 2.00 | Each | 10.00 | 12000.00 | 24000.00 | 9000.00 | 18000.00 | 18000.00 | LAKHANPAL ELECTRIC
124.00 | Material and labour in replacement of 12 Volt, 180 AH maintanance free battery suitable for DG set including trolley stand made out of MS angle iron 40x40x6mm complete all as specified and directed by Eng-in-Charge. | 5.00 | Each | 10.00 | 15000.00 | 75000.00 | 16000.00 | 80000.00 | 75000.00 | R D Bansal
125.00 | Taking down old unserviceable LT Control Panel board and Material & labour indoor type LT control panel 3 phase 4 wire 415 V, 50 Hz of size 1.2 mtr x1.5 mtr x 0.5mtr, 45cm deep made out of powder coated CRCA sheet of size 2mm thick. The panel has compartement type for fixing the accessories and the panel has front and back openable. The panel will be IP 54 protection and lockable with chromium plated 19 mm dia fancy locks having lovers and air vent gasket for natural flow of air.The panel should have aluminium bus bar 1.5 times the rated capacity of incoming MCCB and colour coded on the bus bar and shrinkable sleeve on the bus bar to withstand high resistance. The panel have interconnection of main bus bar and outgoing bus bar. The cubical shell have a bottom channel of size 75x40 mm duly coated with zinc metal. The panel comprising of the following :- | 2.00 | Each Job | 10.00 | 76000.00 | 152000.00 | 90000.00 | 180000.00 | 152000.00 | R D Bansal
125.01 | (i) Incoming MCCB 250 Amp 36 KA, 3 pole-01 No.
125.02 | (ii) Change over switch on load type 250 Amp 4 pole 415 Volts-01 No.
125.03 | (iii) Outgoing MCCB 160 Amp 25 KA, 415 Volts, 3 pole-02 Nos.
125.04 | (iv) Digital voltmeter of size 96X96 mm suitable upto 500 volts-01 No.
125.05 | (v) Digital Ammeter of size 96X96 mm suitable upto 200 Amp-01 No.
125.06 | (vi) LED indicator lamp (RYB)-01 Set of three
125.07 | Note :- (i) The quoted rate shall includes minor items such as lugs, nuts & bolts, washers, top insulators, sleeves, provision of extra holes in bus bar etc. (ii) All internal wiring shall be done with suitable size of PVC insulated solid copper conductor FRLS cable conforming to IS-694. (iii) Panel drawing shall be got approved before placing of order from Accepting Officer.
126.00 | Taking down old unserviceable LT Control Panel board and Material & labour indoor type LT control panel 3 phase 4 wire 415 V, 50 Hz of size 1.2 mtrx1.5 mtr x 0.5mtr, 45cm deep made out of powder coated CRCA sheet of size 2 mm thick. The panel has compartement type for fixing the accessories and the panel has front and back openable . The panel will be IP 54 protection and lockable with chromium plated 19 mm dia fancy locks having lovers and air vent gasket for natural flow of air.The panel should have aluminium bus bar 1.5 times the rated capacity of incoming MCCB and colour coded on the bus bar and shrinkable sleeve on the bus bar to withstand high resistance. The panel have interconnection of main bus bar and outgoing bus bar. The cubical shell have a bottom channel of size 75x40 mm duly coated with zinc metal . The panel comprising of the following :- | 2.00 | Each Job | 10.00 | 67000.00 | 134000.00 | 82000.00 | 164000.00 | 134000.00 | R D Bansal
126.01 | (i) Incoming MCCB 160 Amp 36 KA, 3 pole-01 No.
126.02 | (ii) Change over switch on load type 160 Amp 4 pole 415 Volts-01 No.
126.03 | (iii) Outgoing MCCB 125 Amp 25 KA, 415 Volts, 3 pole-02 Nos.
126.04 | (iv) Digital voltmeter of size 96X96 mm suitable upto 500 volts-01 No.
126.05 | (v) Digital Ammeter of size 96X96 mm suitable upto 200 Amp-01 No.
126.06 | (vi) LED indicator lamp (RYB)-01 Set of three
126.07 | Note :- (i) The quoted rate shall includes minor items such as lugs, nuts & bolts, washers, top insulators, sleeves, provision of extra holes in bus bar etc. (ii) All internal wiring shall be done with suitable size of PVC insulated solid copper conductor FRLS cable conforming to IS-694. (iii) Panel drawing shall be got approved before placing of order from Accepting Officer.
127.00 | Earthing complete with galvanised iron steel plate electrode 600x600x6 mm burried directly in ground vertically in the pit of depth not less than 2.25 mtr below normal ground level with top edge of the plate not less than 1.5 mtr below normal ground level surrounded from all sides with mixture of charcoal and comman salt in alternate layers and electrode connected to galvanised iron strip 25x3 mm by means of nuts bolts. The earth strip protected by 40 mm light grade GI pipe upto test point complete all as shown in electrical plate No 3 of SSR Part I incl 20mm bore medium grade GI pipe for waterring incl PCC chamber on the top of the earth complete all as specified and directed. Note. (i) Cost of excavation, earth work, concrete etc is inclusive in the rate quoted for this item. (ii) Earthing shall be tested and payment will be made only after desired results. | 2.00 | Each Set | 10.00 | 3500.00 | 7000.00 | 3300.00 | 6600.00 | 6600.00 | LAKHANPAL ELECTRIC
128.00 | Supply & fix in replacement of MCCB 3 pole, 415 Volts, 400 Amp, 36 KA complete all as specified and directed. | 1.00 | Each | 10.00 | 15000.00 | 15000.00 | 10000.00 | 10000.00 | 10000.00 | LAKHANPAL ELECTRIC
129.00 | Supply & fix in replacement of MCCB 3 pole, 415 Volts, 250 Amp, 36 KA complete all as specified and directed. | 1.00 | Each | 10.00 | 13000.00 | 13000.00 | 4000.00 | 4000.00 | 4000.00 | LAKHANPAL ELECTRIC
130.00 | Supply & fix in replacement PVC submersible copper cable flat of size 16 Sqmm 3 core including tieing with column pipe with nylon rope complete all as specified and directed. | 180.00 | RM | 10.00 | 490.00 | 88200.00 | 270.00 | 48600.00 | 48600.00 | LAKHANPAL ELECTRIC
131.00 | Description all as per item Ser No 130 above but of size 10 Sqmm 3 core. | 250.00 | RM | 10.00 | 390.00 | 97500.00 | 220.00 | 55000.00 | 55000.00 | LAKHANPAL ELECTRIC
132.00 | Supply & fix in replacement XLPE insulated, armoured heavy duty aluminium conductor 1100Volts grade, cross-sectional area, 120 sqmm 3.5 core complete all as specified and directed. | 175.00 | RM | 10.00 | 409.00 | 71575.00 | 370.00 | 64750.00 | 64750.00 | LAKHANPAL ELECTRIC
133.00 | Description all as per item Ser No 132 above but cross-sectional area, 95 sqmm 3.5 core complete all as specified and directed.. | 250.00 | RM | 10.00 | 373.00 | 93250.00 | 300.00 | 75000.00 | 75000.00 | LAKHANPAL ELECTRIC
134.00 | Description all as per item Ser No 132 above but cross-sectional area, 35 sqmm 3.5 core complete all as specified and directed.. | 400.00 | RM | 10.00 | 193.00 | 77200.00 | 180.00 | 72000.00 | 72000.00 | LAKHANPAL ELECTRIC
135.00 | Description all as per item Ser No 132 above but cross-sectional area, 25 sqmm 3.5 core complete all as specified and directed.. | 350.00 | RM | 10.00 | 148.00 | 51800.00 | 160.00 | 56000.00 | 51800.00 | R D Bansal
136.00 | Excavation in trenches not exc 1.50 metre wide and not exc 1.50 metre deep in soft/ loose soil for laying of UG cable pipe and getting out complete all as specified and directed by Engineer-in-Charge. | 300.00 | Cum | 10.00 | 70.00 | 21000.00 | 50.00 | 15000.00 | 15000.00 | LAKHANPAL ELECTRIC
137.00 | Returning filling in, including spreading levelling, watering and well ramming in layers not exc 25 cm thick complete all as specified and directed. | 250.00 | Cum | 10.00 | 20.00 | 5000.00 | 30.00 | 7500.00 | 5000.00 | R D Bansal
138.00 | Removal of excavated soil surplus to the requirement to a distance n.exc 50 mtr and depositing where directed at a level n.exc 1.5 mtr above the starting point complete all as specified and directed. | 50.00 | Cum | 10.00 | 30.00 | 1500.00 | 50.00 | 2500.00 | 1500.00 | R D Bansal
139.00 | Supply & fix in replacement MCCB 4 pole 415 V adjustable type 160 Amps with breaking capacity 36 KA. Complete all as specified and directed.. | 8.00 | Each | 10.00 | 5800.00 | 46400.00 | 3000.00 | 24000.00 | 24000.00 | LAKHANPAL ELECTRIC
140.00 | Supply & fix in replacement MCCB 4 pole 415 V adjustable type 200 Amps with breaking capacity 36 KA. Complete all as specified and directed.. | 6.00 | Each | 10.00 | 8500.00 | 51000.00 | 3720.00 | 22320.00 | 22320.00 | LAKHANPAL ELECTRIC
141.00 | Supply & fix in replacement MCCB 4 pole 415 V adjustable type 250 Amps with breaking capacity 36 KA. Complete all as specified and directed.. | 5.00 | Each | 10.00 | 11550.00 | 57750.00 | 4000.00 | 20000.00 | 20000.00 | LAKHANPAL ELECTRIC
142.00 | Supply & fix in replacement MCCB 4 pole 415 V adjustable type 350 Amps with breaking capacity 36 KA. Complete all as specified and directed.. | 4.00 | Each | 10.00 | 14800.00 | 59200.00 | 7800.00 | 31200.00 | 31200.00 | LAKHANPAL ELECTRIC
| Total in Figures |  |  |  |  | 1589375.00 |  | 1288670.00
Lowest Amount Quoted BY: LAKHANPAL ELECTRIC(1288670.00)

## BOQ Summary
BOQ Summary Details Tender Title: Repair Maintenance of electrical system including repair and servicing to DG Sets Switchgears and Starters for sewage pumps under GE Utility Ambala Cantt Tender ID: 2018_MES_221529_2
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | LAKHANPAL ELECTRIC | 1288670.00 | L1
| 2 | R D Bansal | 1589375.00 | L2