## BoQ1
eProcurement System for Organisations under MoD Created By: JASBIR SINGH Created Date/Time: 26-Dec-2018 01:18 PM Tender Title: REPAIR AND MAINT OF EXTERNAL ELECTRIFICATION WORKS AND CERTAIN OTHER MISC WORKS AT 3BRD AF STN UNDER GE AF MC CHANDIGARH Tender ID: 2018_MES_222492_2
Tender Inviting Authority: GE (AF) MC CHANDIGARH
Name of Work: REPAIR AND MAINT OF EXTERNAL ELECTRIFICATION WORKS AND CERTAIN OTHER MISC WORKS AT 3BRD AF STN UNDER GE AF MC CHANDIGARH
Contract No: GE(AF) MC/CHD- 40 /2018-19(Tender Id : 2018_MES_222492_1)
SCHEDULE OF WORK / ITEM(S)
Sl.No | Description of Work / Item(s) | No.of Qty | Units | Estimated Rate | R D Bansal |  | Raman Electric Trading Co |  | Arun enterprises |  | HARISH SALES CORPORATION |  | M/s badrinath Traders |  | HORIZON CONSTRUCTION COMPANY |  | Shree Balaji Construction
[5 empty] | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | Rate | Amount | L1 Amount | L1 Vendor
1.00 | XLPE insulated, screened, PVC bedded, galvanised steel strip or wire armoured, electric cables (heavy duty) stranded aluminium conductor including cable glands, cable lugs etc , to suit the cable size, 1100 volt grade, ISI marked, laid in trenches or fixing along the poles or passing through the pipes or laid under floors or through walls/ducts etc. 'IN REPAIR' complete all ll as specified and directed by Engineer-in-Charge of following cross sectional area :- NOTE: Excavation, earth work, sand cushioning, cable cover & pipe for cable protection shall be measured and paid for separately.
1.01 | Cross sectional area 120 sq. mm, 3.5 core | 450.00 | Running Metre | 100.00 | 445.00 | 200250.00 | 377.00 | 169650.00 | 480.07 | 216031.50 | 550.00 | 247500.00 | 440.00 | 198000.00 | 410.00 | 184500.00 | 530.00 | 238500.00 | 169650.00 | Raman Electric Trading Co
1.02 | Cross sectional area 95 sq. mm, 3.5 core | 1500.00 | Running Metre | 100.00 | 337.00 | 505500.00 | 300.00 | 450000.00 | 370.00 | 555000.00 | 450.00 | 675000.00 | 355.00 | 532500.00 | 200.00 | 300000.00 | 420.00 | 630000.00 | 300000.00 | HORIZON CONSTRUCTION COMPANY
1.03 | Cross sectional area 25 sq. mm, 3.5 core | 820.00 | Running Metre | 10.00 | 148.00 | 121360.00 | 130.00 | 106600.00 | 140.05 | 114841.00 | 200.00 | 164000.00 | 135.00 | 110700.00 | 200.00 | 164000.00 | 180.00 | 147600.00 | 106600.00 | Raman Electric Trading Co
1.04 | Cross sectional area 16 sq. mm, 4 core | 550.00 | Running Metre | 10.00 | 120.00 | 66000.00 | 130.00 | 71500.00 | 110.00 | 60500.00 | 150.00 | 82500.00 | 112.00 | 61600.00 | 170.00 | 93500.00 | 130.00 | 71500.00 | 60500.00 | Arun enterprises
1.05 | Cross sectional area 70 sq. mm, 3.5 core | 950.00 | Running Metre | 100.00 | 292.00 | 277400.00 | 265.00 | 251750.00 | 270.01 | 256509.50 | 350.00 | 332500.00 | 295.00 | 280250.00 | 290.00 | 275500.00 | 380.00 | 361000.00 | 251750.00 | Raman Electric Trading Co
1.06 | Cross sectional area 50 sq. mm, 3.5 core | 350.00 | Running Metre | 100.00 | 229.00 | 80150.00 | 200.00 | 70000.00 | 220.06 | 77021.00 | 270.00 | 94500.00 | 220.00 | 77000.00 | 240.00 | 84000.00 | 255.00 | 89250.00 | 70000.00 | Raman Electric Trading Co
1.07 | Cross sectional area 300 sq. mm, 3.5 core | 200.00 | Running Metre | 10.00 | 193.00 | 38600.00 | 870.00 | 174000.00 | 800.02 | 160004.00 | 1250.00 | 250000.00 | 1000.00 | 200000.00 | 603.00 | 120600.00 | 1200.00 | 240000.00 | 38600.00 | R D Bansal
1.08 | Cross sectional area 400 sq. mm, 3.5 core | 200.00 | Running Metre | 10.00 | 1300.00 | 260000.00 | 1390.00 | 278000.00 | 800.02 | 160004.00 | 1600.00 | 320000.00 | 1270.00 | 254000.00 | 900.00 | 180000.00 | 1530.00 | 306000.00 | 160004.00 | Arun enterprises
1.09 | Cross sectional area 10 sq. mm, 4 core | 350.00 | Running Metre | 10.00 | 100.00 | 35000.00 | 120.00 | 42000.00 | 100.00 | 35000.00 | 130.00 | 45500.00 | 100.00 | 35000.00 | 130.00 | 45500.00 | 115.00 | 40250.00 | 35000.00 | Arun enterprises, M/s badrinath Traders, R D Bansal
1.10 | Cross sectional area 185 sq. mm, 3.5 core | 350.00 | Running Metre | 10.00 | 607.00 | 212450.00 | 560.00 | 196000.00 | 500.05 | 175017.50 | 900.00 | 315000.00 | 650.00 | 227500.00 | 653.00 | 228550.00 | 780.00 | 273000.00 | 175017.50 | Arun enterprises
2.00 | Boring of holes under road, pavement, hard standing by drilling for laying of 50/80mm GI pipe for cable or laying electric cable of any size complete all as directed. | 70.00 | Running Metre | 10.00 | 200.00 | 14000.00 | 250.00 | 17500.00 | 46.00 | 3220.00 | 400.00 | 28000.00 | 100.00 | 7000.00 | 200.00 | 14000.00 | 200.00 | 14000.00 | 3220.00 | Arun enterprises
3.00 | Supply, install in repair, testing and commissioning of factory made LT feeder pillar box, CPRI approved, ourdoor type, 1.1KV made out of MS CRCA sheet 3mm thick, having 4 Nos Aluminium bus bar of size 200AMp for phase 100 Amp for neutral fixed on LT, 8 Nos insulators of size 0.60M x 0.45 M with legs made out of MS angle 50x50x5mm & 0.75mtr in length, locking arrangements front and back opening danger notice board with skull & bone monogram and indicating 1100 volt danger board including incoming and outgoing connections and testing on completion complete all as directed. | 20.00 | Each | 10.00 | 4000.00 | 80000.00 | 7500.00 | 150000.00 | 5000.05 | 100001.00 | 11000.00 | 220000.00 | 7500.00 | 150000.00 | 5600.00 | 112000.00 | 6000.00 | 120000.00 | 80000.00 | R D Bansal
4.00 | Junction box of size 300x300x150mm, fixed in repair, made out of 2.0mm thick MS CRCA sheet, having front openable and locable hinged shutter with self closing arrangmenet, outdoor type weather and vermin proof completed duly painted with two coats of silver enameled paint over a coat of red oxide primer, comprising with insualted aluminium bus bar 03 Nos 63Amp 1 neutral strip suitable for 4 wire system, single phase 230 Volts of size 20x3 mm mounted on porcelain based insulators, having arrangement of connecting incoming and outgoing cables in and including MCB SP 'C' curve 06 Amp, 240 Volts, 10 KA mounted on Din rail, thimbles etc. complete with and including suitable size of cable glands and MS clamps, nuts, bolts and washers complete all as specified and directed by Engineer-in-Charge. | 100.00 | Each | 10.00 | 600.00 | 60000.00 | 920.00 | 92000.00 | 900.01 | 90001.00 | 900.00 | 90000.00 | 700.00 | 70000.00 | 700.00 | 70000.00 | 800.00 | 80000.00 | 60000.00 | R D Bansal
5.00 | Tubes, light grade', galvanised, for the following bore, or cable protection, 'IN REPAIR' complete all as specified and directed.
5.01 | 50mm dia | 110.00 | Running Metre | 10.00 | 190.00 | 20900.00 | 200.00 | 22000.00 | 190.00 | 20900.00 | 250.00 | 27500.00 | 159.00 | 17490.00 | 220.00 | 24200.00 | 450.00 | 49500.00 | 17490.00 | M/s badrinath Traders
5.02 | 80mm dia | 50.00 | Running Metre | 10.00 | 300.00 | 15000.00 | 300.00 | 15000.00 | 370.00 | 18500.00 | 600.00 | 30000.00 | 259.00 | 12950.00 | 340.00 | 17000.00 | 700.00 | 35000.00 | 12950.00 | M/s badrinath Traders
5.03 | 40mm dia | 70.00 | Running Metre | 10.00 | 140.00 | 9800.00 | 170.00 | 11900.00 | 181.00 | 12670.00 | 200.00 | 14000.00 | 130.00 | 9100.00 | 260.00 | 18200.00 | 350.00 | 24500.00 | 9100.00 | M/s badrinath Traders
5.04 | 20mm dia | 210.00 | Running Metre | 10.00 | 90.00 | 18900.00 | 60.00 | 12600.00 | 46.00 | 9660.00 | 150.00 | 31500.00 | 90.00 | 18900.00 | 100.00 | 21000.00 | 170.00 | 35700.00 | 9660.00 | Arun enterprises
6.00 | Earthing complete with galvanized steel earth plate electrode 600 mm x 600 mm x 6 mm thick buried directly in ground vertically in a pit of depth not less than 2.25 metre below ground levels with top edge of the earth plate not less than 1.50 metre below normal ground level surrounded from all sides by mixture of charcoaland common salt and electrode connected to and including galvanized iron earth strip, 32 x 6 mm by means of bolts, nuts check nuts and washers of galvanised steel including GI pipe light grade 40mm dia for protection pipe and GI pipe medium grade 20mm dia bore for watering funnel with wire mesh. 80mm thick precast RCC 1:1.5:3 type A1 cover with frame duly reinforced with XPM (weight not less than 3kg/sqm), PCC chamber pit with PCC 1:3:6 type C-2 excavation and earth work all as shown in electrical plate No 3 connected to earthing test point complete all as specified and directed by Engineer-in-Charge. Note : The unit rate includes for protecton pipe 40mm and GI earth strip 32 x 6mm from top of earth plate upto 7.50 metre above ground level. | 34.00 | Each Set | 10.00 | 2500.00 | 85000.00 | 3000.00 | 102000.00 | 2000.08 | 68002.72 | 4000.00 | 136000.00 | 2800.00 | 95200.00 | 2800.00 | 95200.00 | 3200.00 | 108800.00 | 68002.72 | Arun enterprises
7.00 | Supplying and laying or fixing or passing through pipe, 1100 volts grade heavy duty cable with PVC insulated and PVC sheathed multi stranded copper conductor cable 2x2.5 sqmm and 1x1.5 sqmm for earth wire single core 1100 V to keep inside of GI pipe of pole for connection from junction box to street light fitting etc complete all as specified and as directed by Engineer-in-Charge. | 500.00 | Running Metre | 10.00 | 45.00 | 22500.00 | 30.00 | 15000.00 | 9.01 | 4505.00 | 100.00 | 50000.00 | 40.00 | 20000.00 | 15.00 | 7500.00 | 60.00 | 30000.00 | 4505.00 | Arun enterprises
8.00 | Supply, install, testing and commissioning of factory made LT panel board, CPRI approved, ourdoor type, LT distribution switch gear and control gear, leg mounted, totally enclosed, cubical type modular compartment, dust and vermin proof with neoprene gasket, fabricated out of CRCA sheet of thickness 3mm complete with bus bar chamber having openable front and rear shutters with suitable locking arrangement of shutters, duly powder coated rust proofing incluidng PCC 1:2:4 type B1 suing 20mm graded stone aggregate foundation raised base complete all as specified and directed. The items includes making all connections of incoming and out going cable feeders with suitable size lugs, glands etc. The panel should have base frame made out of equal angles 50mm x 50mm x 6mm errected with and including PCC 1:3:6 at a depth 30cm below ground level and 30cm above ground level including necessary earth work complete. The overall size of the LT panel 0.90m x 1.00m x .45m and including consists of the following accessories: - | 5.00 | Each Job | 10.00 | 67000.00 | 335000.00 | 81000.00 | 405000.00 | 120007.00 | 600035.00 | 140000.00 | 700000.00 | 55000.00 | 275000.00 | 98000.00 | 490000.00 | 70000.00 | 350000.00 | 275000.00 | M/s badrinath Traders
8.01 | Aluminium bs bar four wire system 415 volt mounted on porcelain heat shrinkable insulator sleeve sitable for 800A for phases and 400A for neutral
8.02 | Indicator lamps for all the three phase with different coour LED lamp red, yellow and green - 01 Set
8.03 | One set of volt meter size 96mm x 96mm flush type digital of rating 0 to 500 volt with selector switches
8.04 | One Set of amm meter size 96mm x 96mm flush type digital with CT operated suitable for 0-800Amp
8.05 | Danger notice board of size 200mm x 150mm x 1.6mm thick MS sheet, vitreous enamelled white and letter figure and convention skull and bones of signal red colour and fixed/riveted with panel - 02 Nos
8.06 | INCOMING:
8.07 | MCCB TPN 415 volt adjustable thermal and magnetic setting 400Amp, 35kA beaking capacity - 01 No Adjustable thermal magnetic with extended. Make : Havells or equivalent in IndoAsina/ ABB /Siemes/Legrand/Hager
8.08 | OUTGOING:
8.09 | MCCB TPN 415 volt adjustable thermal and magnetic setting 250Amp, 25kA beaking capacity - 01 No Adjustable thermal magnetic. Havells or equivalent in IndoAsina/ ABB /Siemes/Legrand/Hager
8.10 | MCCB TPN 415 volt adjustable thermal and magnetic setting 200Amp, 25kA breaking capacity - 01 No Adjustable thermal magnetic. Make : Havells or equivalent in IndoAsina/ ABB /Siemes/Legrand/Hager
8.11 | Cable alleys
8.12 | Cable glands to adopt incoming and outgoing cables
9.00 | Dismantling /Taking out LT cable from pole and connect on LT panel /LT bus bar including thimble as required at site complete all as directed. | 15.00 | Each Job | 10.00 | 100.00 | 1500.00 | 300.00 | 4500.00 | 55.00 | 825.00 | 150.00 | 2250.00 | 100.00 | 1500.00 | 470.00 | 7050.00 | 110.00 | 1650.00 | 825.00 | Arun enterprises
10.00 | Excavation in trenches in soft/loose soil not exceeding 1.50 meter wide and not exceeding 1.50 meter in depth and not exceeding 10Sqm on plan and getting out complete, laying of pipe and cable including taking out old pipes/bricks complete all as specified. | 510.00 | Cubic Metre | 10.00 | 76.00 | 38760.00 | 80.00 | 40800.00 | 70.03 | 35715.30 | 150.00 | 76500.00 | 80.00 | 40800.00 | 80.00 | 40800.00 | 65.00 | 33150.00 | 33150.00 | Shree Balaji Construction
11.00 | Returning, filling in, including spreading, leveling, watering and well ramming in layers not exc 25 cm thick each, excavated soil in trenches complete as in soft/loose soil, complete all as specified. | 310.00 | Cubic Metre | 10.00 | 10.00 | 3100.00 | 20.00 | 6200.00 | 4.05 | 1255.50 | 40.00 | 12400.00 | 20.00 | 6200.00 | 25.00 | 7750.00 | 10.00 | 3100.00 | 1255.50 | Arun enterprises
12.00 | Removing of surplus soil/ excavated material to a distance not exceeding 50 metre and depositing where directed at a level not exceeding 1.5m above the starting point complete all as specified. | 95.00 | Cubic Metre | 10.00 | 15.00 | 1425.00 | 20.00 | 1900.00 | 5.05 | 479.75 | 50.00 | 4750.00 | 30.00 | 2850.00 | 70.00 | 6650.00 | 15.00 | 1425.00 | 479.75 | Arun enterprises
13.00 | Clean dry sand laid in trenches/ducts for bedding and cushioning to cable, 8cm in depth before laying the cable and 15 cm in depth after laying the cable including spreading, levelling and consolidation complete all as specified and directed. Note : Consolidated/punned sand shall be measured for payment purpose. | 150.00 | Cubic Metre | 10.00 | 340.00 | 51000.00 | 340.00 | 51000.00 | 100.00 | 15000.00 | 500.00 | 75000.00 | 350.00 | 52500.00 | 800.00 | 120000.00 | 550.00 | 82500.00 | 15000.00 | Arun enterprises
14.00 | Bricks common burnt clay building bricks, sub class 'B' , Designation 75 , laid adjacent to each other length wise perpendicular to the central axis of cable complete all as specified and directed. | 18.00 | Per 1000 Nos | 10.00 | 3000.00 | 54000.00 | 3000.00 | 54000.00 | 2500.03 | 45000.54 | 5000.00 | 90000.00 | 2500.00 | 45000.00 | 3500.00 | 63000.00 | 3500.00 | 63000.00 | 45000.00 | M/s badrinath Traders
15.00 | Energy LED street light fittings of 70W capacity, 'IN REPAIR' high pressure die cast aluminium housing with seal toughened glass cover. Light source should be multi LED SMD array with individual secondary lenses, colour temperature 6000K ± 500K, System efficiency should be minimum 100 lumens/watt and minium system lumen package of 7000 lumens at LM 79 complete all as directed. | 30.00 | Each | 10.00 | 3730.00 | 111900.00 | 3900.00 | 117000.00 | 3205.00 | 96150.00 | 4500.00 | 135000.00 | 4200.00 | 126000.00 | 3500.00 | 105000.00 | 4000.00 | 120000.00 | 96150.00 | Arun enterprises
16.00 | Dismantling of ACSR conductor any size complete all as directed. | 5.00 | Quintal | 10.00 | 100.00 | 500.00 | 200.00 | 1000.00 | 500.05 | 2500.25 | 500.00 | 2500.00 | 100.00 | 500.00 | 50.00 | 250.00 | 200.00 | 1000.00 | 250.00 | HORIZON CONSTRUCTION COMPANY
17.00 | Dismantling of cross arms of any size complete all as directed. | 3.00 | Quintal | 10.00 | 100.00 | 300.00 | 100.00 | 300.00 | 500.05 | 1500.15 | 500.00 | 1500.00 | 100.00 | 300.00 | 30.00 | 90.00 | 500.00 | 1500.00 | 90.00 | HORIZON CONSTRUCTION COMPANY
18.00 | Dismantling of insulators of any type complete all as directed. | 120.00 | Each | 10.00 | 2.00 | 240.00 | 2.00 | 240.00 | 1.00 | 120.00 | 30.00 | 3600.00 | 10.00 | 1200.00 | 10.00 | 1200.00 | 5.00 | 600.00 | 120.00 | Arun enterprises
19.00 | Preparation of rusted surfaces of steel pole with brackets of any size/shape/type at any height and painting with aluminium paint and alternate colour of sky blue, 3 strip and white paint 2 strip of 30cm height at bottom of the pole (approx 1.5mtr) and numbering the pole (with 5cm height) black paint with back background and letter with yellow paint10 cm dia round complete all as directed. | 100.00 | Each | 10.00 | 200.00 | 20000.00 | 250.00 | 25000.00 | 100.00 | 10000.00 | 300.00 | 30000.00 | 200.00 | 20000.00 | 350.00 | 35000.00 | 120.00 | 12000.00 | 10000.00 | Arun enterprises
20.00 | GI Pipe bracket made out of 40mm dia light grade, FIXED IN REPAIR, fabricated into shape and size as required not less than 1.20mtr long complete with and including 02 Nos MS clamp of MS flat iron 40x6mm with bolts, nuts and washer coplete fixed on pole/wall complete all as directed. | 100.00 | Each | 10.00 | 200.00 | 20000.00 | 300.00 | 30000.00 | 150.04 | 15004.00 | 550.00 | 55000.00 | 250.00 | 25000.00 | 500.00 | 50000.00 | 550.00 | 55000.00 | 15004.00 | Arun enterprises
21.00 | Energy saving LED street light fittings, FIXED IN REPAIR, 45W capacity, high pressure die cast aluminium housing with seal toughened glass cover light source should be multi LED SMD array with individual secondary lenses, colour temperature 6000K ± 500K, SYSTEM Efficiency should be minium 100 Lumens/watt and minium system lumen package of 4500 lumens as LM9 complete all as directed. | 30.00 | Each | 10.00 | 1750.00 | 52500.00 | 2300.00 | 69000.00 | 2107.00 | 63210.00 | 3300.00 | 99000.00 | 3000.00 | 90000.00 | 2000.00 | 60000.00 | 2700.00 | 81000.00 | 52500.00 | R D Bansal
22.00 | NOTE: For arriving contract sum, the amount of credit schedule is to be deducted from the total amount in the General Summary.
| Total in Figures |  |  |  |  | 2813035.00 |  | 3053440.00 |  | 3024183.71 |  | 4441000.00 |  | 3064040.00 |  | 3042040.00 |  | 3700525.00
Lowest Amount Quoted BY: R D Bansal(2813035.00)

## BOQ Summary
BOQ Summary Details Tender Title: REPAIR AND MAINT OF EXTERNAL ELECTRIFICATION WORKS AND CERTAIN OTHER MISC WORKS AT 3BRD AF STN UNDER GE AF MC CHANDIGARH Tender ID: 2018_MES_222492_2
Sheet Name | Sl.No | Bidder Name | Amount | Bid Rank
BoQ1 | 1 | R D Bansal | 2813035.00 | L1
| 2 | Arun enterprises | 3024183.71 | L2
| 3 | HORIZON CONSTRUCTION COMPANY | 3042040.00 | L3
| 4 | Raman Electric Trading Co | 3053440.00 | L4
| 5 | M/s badrinath Traders | 3064040.00 | L5
| 6 | Shree Balaji Construction | 3700525.00 | L6
| 7 | HARISH SALES CORPORATION | 4441000.00 | L7